ITEM NO. 07 (B-34)

1.	Name of Work: Purchase of Distribution Transformers 1600KVA Dry Type (Cast Resin) 10.5/0.415 KV.

2.	Department 	: 	ELECTRICITY DEPARTMENT

3.	Brief History of the Proposal: A case for purchase of 20 Nos. Distribution Transformers 1600KVA Dry Type (Cast Resin) 10.5/0.415 KV was processed against the sanctioned estimate duly approved by council vide Reso. No.10 (B-37) dt. 19.3.2010.

4. 	Detailed Proposal of the Subject: Tenders were invited in three cover system from the manufacturers only through e-procurement system for the purchase of 20 Nos. Distribution Transformers 1600KVA Dry Type (Cast Resin) 10.5/0.415 KV by giving due publicity to the tender as per the codal provisions. In response to the Tender Enquiry, offers of the following five firms were received on due date of opening i.e.23.07.10.

1.	M/s Ames Impex Electricals Pvt. Ltd.

2.	M/s Areva T & D India Ltd.

3.	M/s Megawin Switchgear (P) Ltd.

4.	M/s Vijai Electrical Ltd.

5.	M/s Voltamp Transformers Ltd.

The offers of the above firms were scrutinized and subsequently examined by the planning division and the price bids of three eligible participant firms i.e. M/s Ames Impex Electricals Pvt. Ltd, M/s Megawin Switchgear (P) Ltd & M/s Voltamp Transformers Ltd. were opened through e-procurement system on dated 20.10.10.  The detailed position of the firms explained below:-

| S.No. | Name of the Tendering Firms | 1600 KVA, 10.5/0.415 KV Distribution Transformer Dry Type (Resin Cast) Qty=20Nos. Basic Rate for Unit Transformer | Excise Duty @ 10.3% (Rs.) | CST @ 2% against form ‘C’ (Rs.) | Freight (Rs.) | Insurance (Rs.) | Computed Unit Price (Rs.) | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1. | M/s Voltamp Transformers Ltd. | Rs.17,30,000.00 | 1,78,190/- | 38,163.80 | 12,500/- | 5,500/- | 19,64,353.80 | Rates of the L-I firm M/s Megawin Switchgear (P) Ltd. are 3.13% above the estimated cost put to tender |
| 2. | M/s AMES Impex Electrical Pvt. Ltd. | Rs.13,32,000.00 | 1,37,196/- | 29,383.92 | 22,000/- | 1,521/- | 15,22,100.92 |  |
| 3. | M/s Megawin Switchgear (P) Ltd | Rs.13,00,000.00 | 1,33,900/- | 28,678.00 | 20,000/- | 2,000/- | 14,84,578.00 |  |
| 4. | M/s Areva T & D India Ltd. | The firm did not meet the NIT requirement hence their offer was ignored. |
| 5. | M/s Vijai Electrical Ltd. | The firm did not meet the NIT requirement hence their offer was ignored. |

Based on the computed cost of the each tendering firm, capitalized cost has been worked out to evaluate the position of lowest tendering firm as per the provision in the NIT as explained below:-

Capitalized Cost:-

| Name of the Firm | Computed Rates | No Load Losses | Load Losses | Capitalized unit price | Capitalized Cost for 20 Nos. Trf. |
| --- | --- | --- | --- | --- | --- |
| M/s Voltamp Transformers Ltd. | Rs.19,64,353.80 | 2.6 KW | 9.0 KW | Rs.33,14,046.42 | Rs.6,62,80,928.4 |
| M/s Ames Impex Electricals Pvt. Ltd | Rs.15,22,100.92 | 2.3 KW | 12.0KW | Rs.30,70,713.43 | Rs.6,14,14,268.6 |
| M/s Megawin Switchgear (P) Ltd | Rs.14,84,578.00 | 2.4 KW | 9.5 KW | Rs.28,35,155.38 | Rs.5,67,03,107.6 |

M/s Megawin Switchgear (P) Ltd has emerged as a lowest tendering firm with their quoted basic rate Rs.13,00,000.00 (Ex works) + Excise duty @ 10.3% + CST @ 2% against form ‘C’ + Freight Rs.20,000.00 & Insurance Rs. 2,000.00 per transformer. The computed unit price of transformer has been worked out to Rs.14,84,578.00. The total computed cost for the purchase of 20 No. transformer has been worked out to Rs.2,96,91,560.00 which is 3.13% above the estimated cost  put to the tender based on LPR dt.03.03.10.

Justification statement based on the current market rate has been prepared and is tabulated as under:-

| Description of item | Rates of the L-I firm M/s Megawin Switchgear (P) Ltd (Ex-works Rate) | Justified rates based on the current market rates obtained from M/s Daua Transformer Udhyog (P) Ltd.(Ex-works Rate) | Remarks |
| --- | --- | --- | --- |
| 1600 KVA, 10.5/0.415 KV Distribution Transformer Dry Type (Resin Cast) Qty=20Nos. | Rs. 13,00,000.00 Each | Rs.14,90,000.00 Each | Rates of the L-I firm M/s Megawin Switchgear (P) Ltd. is 12.75 % below than the current market rate. |

The rates of the lowest tendering firm M/s Megawin Switchgear (P) Ltd are competitive, lowest, reasonable and hence justified.

The case was examined by the Planning and subsequently concurred by Finance vide dairy No.   2736 / Finance  Dt. 10.1.2011.

5.	Financial Implications: Rs.2,96,91,560.00 (Rs. Two crore Ninety Six lacs Ninety One thousand Five hundred Sixty rupees only),(Rs. 14,84,578 x 20) inclusive of all prevalent taxes, duties, freight, insurance, packing & handling.

6.     	Implementation Schedule: Commencing with 10 Nos. within two months and completion @ 10 Nos. per month thereafter and completion in three months from the date of approval of drawings to be submitted with in 15 days from the date of issue of supply order.

- Comments of the Finance Department: Finance vide Diary No. 2736/Finance  dt. 10.1.2011 has concurred in the proposal with no further comments.

- Comments of the Department on comments of Finance Deptt. :

Nil.

9.	Legal Implication of the Subject:

Nil

10.	Details of previous Council Resolution:

Nil

11.	Comments of Law Department:

Nil

12.	Comments of the department on the comments of Law Department:	       Nil

13.	Certification by the Department:

All Central Vigilance Commission (CVC) guidelines have been followed.

14.	Recommendations of the Department: The case may be placed before the Council for the purchase of 20Nos. Distribution Transformers 1600KVA Dry Type (Cast Resin) 10.5/0.415 KV from the lowest tendering firm M/s Megawin Switchgear (P) Ltd  with their quoted basic rate Rs.13,00,000.00 (Ex works) + Excise duty @ 10.3% + CST @ 2% against form ‘C’ + Freight Rs.20,000.00 & Insurance Rs. 2,000.00 per transformer. The computed unit price of transformer has been worked out to Rs.14,84,578.00. The total computed cost for the purchase of 20Nos. transformer has been worked out to Rs.2,96,91,560.00 on the terms, conditions and specifications of NIT. Since the material requirement is of urgent nature, approval may also be accorded to place Supply Orders on the firm in anticipation of the confirmation of the minutes of the Council meeting.

15.	Draft Resolution: Resolved by the Council that the approval is accorded to the purchase of 20Nos. Distribution Transformers 1600KVA Dry Type (Cast Resin) 10.5/0.415 KV from lowest tendering firm M/s Megawin Switchgear (P) Ltd with their quoted basic rate Rs.13,00,000.00 (Ex works) + Excise duty @ 10.3% + CST @ 2% against form ‘C’ + Freight Rs.20,000.00 & Insurance Rs. 2,000.00 per transformer. The computed unit price of transformer has been worked out to Rs.14,84,578.00. The total computed cost for the purchase of 20 No. transformer has been worked out to Rs.2,96,91,560.00 on the terms, conditions and specifications of NIT. Approval is also accorded to place Supply Orders on the firm in anticipation of the confirmation of the minutes of the Council meeting.

COUNCIL’S DECISION

Resolved by the Council to accord approval to the purchase of 20Nos. distribution Transformers 1600KVA Dry Type (Cast Resin) 10.5/0.415 KV from lowest tendering firm M/s Megawin Switchgear (P) Ltd with their quoted basic rate of Rs.13,00,000.00 (Ex works) + Excise duty @ 10.3% + CST @ 2% against form ‘C’ + Freight Rs.20,000.00 & Insurance Rs.2,000.00 per transformer at the computed unit price of transformer worked out to Rs.14,84,578.00 and  total computed cost for the purchase of 20 No. transformer worked out to Rs.2,96,91,560.00; on the terms, conditions and specifications of NIT.

It was also resolved that further action may be taken by the Department in anticipation of confirmation of the Minutes by the Council.