ITEM NO. 04 (B-13)

(1) 	Name of the work :	Improvement of LT network around Akbar Road, New Delhi.

(2) 	Name of the Department  :  Electricity

(3) 	Brief History of the case :

Subsequent to frequent power trippings observed in the area around Akbar Road and Maulana Azad Road, a survey of the area was carried out by the team of E. E.(E)(P.11KV), E.E.(D/S) and E.E.(M/S). The existing LT network in the area starting from Meena Bagh (near Sunehri Masjid) upto Moti Lal Nehru Place, area around Vice President House along Maulana Azad Road and Akbar road has not been augmented  for more than five years.   It was observed that the electrical load of the area is increasing day by day due to installation of a number of new air-conditioners and other electrical gadgets.  Due to inadequate size of LT network, low voltage and over-heating of cables is a common phenomenon. The area is inhabited by VIPs & sensitive Govt. offices. The existing LT system of the area is unable to cope with the increased electrical load.  There is no Electric Substation in this area and power supply is brought from distant Sub-stations. In a meeting attended by SE (E-II), EE(M/S), EE(D/S) & EE(P-11KV) it was decided that 1 x 990 KVA Unitized Sub-station may be installed in the area to augment the LT system of the area.  The tentative location of the proposed Unitized Sub-station has also been decided in consultation with stake holders.

(4)  	Detailed proposal on the Project :

- 1 x 990 KVA Unitized Sub-station is proposed to be installed with ring main unit having three SF-6 /1VCB breaker (2 incoming & 1 outgoing).

- This Unitized Sub-station is to be provided with two HT feeds each of size 400sq.mm/3C.  One HT feed of about 1750 m length is proposed to be laid down from Sub-station Pandara Park and the other of about 1300 m length from Sub-station Nirman Bhawan.

- Two big size GS pillars are proposed to be installed outside to take care of surrounding CPWD Bnglows along Akbar Road at locations to be decided by E.E.(D/S) in consultation with E.E.(M/S) during execution of the work.  These GS pillars would be connected with the Unitized Sub-station through LT XLPE cable of size 400 sq.mm/3-½ C.

- Two HT panels one each at Sub-station Pandara Park and Sub-station Nirman Bhawan are proposed to be installed for providing HT feeds to the proposed Unitized Sub-station.

(5)	Financial implications : Financial implications in the proposal is estimated to be Rs.1,06,63,500/-.

(6)	Implementation schedule: 4 months

(7)	Comments of the Finance Deptt. on the subject :

The Finance Deptt. vide Dy. No. 1585/PS/FA/DLO  dated 15-7-10 have concurred in the estimate with no further comments.

(8)	Comments of the Deptt. on the Comments of the Finance  Deptt. : NIL

(9)	Legal implication of the Project : -   NIL

(10)	Details of previous Council Resolution :	NIL

(11)	Comments of  Law Deptt. :  	NIL

(12)	Comments of the Deptt. on the comments of Law Deptt. :  NIL

(13)	Certification by the Deptt. that all Central Vigilance Commission (CVC) guidelines have been followed : It is certified that all Central Vigilance Commission (CVC) guidelines have been followed in processing the case.

(14)	Recommendation  : The estimate amounting to Rs.1,06,63,500/- for Improvement of LT network around Akbar Road, New Delhi may be placed before the Council to accord administrative approval and expenditure sanction.  Since the work is of urgent nature, approval is solicited to take further action in anticipation to confirmation of the Minutes of Council Meeting.

(15)	Draft Resolution : Resolved by the Council that Administrative approval and expenditure sanction is granted to the estimate amounting to Rs.1,06,63,500/- for Improvement of LT network around Akbar Road, New Delhi.  Further approval is accorded  to take further action in anticipation to confirmation of the Minutes of Council Meeting.

COUNCIL’S DECISION

Resolved by the Council to accord administrative approval and expenditure sanction to the estimate amounting to Rs.1,06,63,500/- for Improvement of LT network around Akbar Road, New Delhi.

It was also resolved that further action may be taken by the Department in anticipation of confirmation of the Minutes by the Council.