ITEM NO. 08 (B-26)

- NAME OF WORK-

REPLACEMENT OF OLD PILCA CABLE WITH 33KV, 400 SQMM/3C, XLPE FROM 66KV ESS VIDYUT BHAWAN TO 66KV ESS SCHOOL LANE AND FROM 66KV ESS SCHOOL LANE TO 33KVESS CONNAUGHT PLACE.

- Name of the Department- ELECTRICITY DEPARTMENT

- Brief history of the proposals-

In 1982 a  33KV, 400 Sq.mm/3C PILCA Cable ESS laid from 33KV ESS Connaught Place to 66KV ESS Vidyut Bhawan and the same was LILO at 66KV ESS School Lane in the year of 2001. The prescribed life of the feeder is 35 Years and the same has served only 27 Years. As per details furnished by EE (M-33KV) that the existing feeder is suffering with a number of joints thus deteriorated the load transferring capacity of the feeder.

To make the system more reliable and flexible, PILCA cable from 66KV  ESS Vidyut Bhawan to 66KV ESS School lane and 66KV ESS School lane to 33KV ESS Connaught Place need to be replaced. As per reliability concerned the existing feeder can’t be relied to transmit the power during the Commonwealth Game. In case of outage at any one of the ESS, existing feeder is to be utilized to restore the power supply which has less capacity & deteriorated as the No. of joints are more and unable to give its Performance upto full load capacity. Therefore it is proposed to replace the said cable with 400Sq.mm/3C, XLPE. The Proposed cable of 400Sq.mm/3C, XLPE shall be able to transmit 18MVA (app.) among the ESS. Further the existing cable shall be dismantled wherever it is economical, considering the road civil & road restoration charges. . The credit of the same shall be given at the time of execution by the executing division.

- Detailed proposal on the Project-

To restore the electric supply through the cable among ESS School lane, Vidyut Bhawan and Connaught Place following is be proposed

- 33KV, 400Sq.mm/3C, XLPE Cable from ESS Vidyut Bhawan to ESS School Lane ( 4.5 Km.)

- 33KV, 400Sq.mm/3C, XLPE Cable from ESS School Lane to ESS Vidyut Bhawan ( 0.9 Km.)

Accordingly an estimate amounting to Rs.188.78 including 3% contingencies has been prepared to cover the cost of the replacement work.

- Financial Implications-

The estimated cost for replacement of 33KV400mm2 XLPE Cable from ESS Vidyut Bhawan to ESS School Lane and ESS School Lane to ESS Connaught Place Rs. 188.78 Lacs chargeable to the head of a/c E.3.1

- Implementation schedule with timeliness for each stage including internal processing: -.

i)	Approval of scheme by Council	December, 2009

ii)	Issue of estimate to Maintenance

Division for execution	December, 2009

iii)	Preparation of detailed estimate	January, 2010

iv)	Approval of Draft NIT	February, 2010

v)	Call of tenders	April 2010

vi)	Award of work including opening

of tenders, negotiations with the 	May, 2010

tenderer etc.

vii)	Completion of work	July, 2010

The scheme shall be executed departmentally; tentative schedule of time of completion the project is September 2010.

7.		Comments of the Finance Department on the subject-

The finance Deptt. Vide diary No. 4156/PS/FA/D/2009 Dated 11.11.2009 has concurred in the preliminary estimate amounting to Rs. 188.78 Lacs with no further comments.

- Comments of the Department on comments of Finance Deptt:

Nil

- Legal implications of the Project: -   No legal implication involved.

10.	Details of Previous Council Resolution- Nil

11.	 Comments of the Law Deptt. on the Project:  Nil

12.   Comments of the deptt. on the Law Deptt    Nil

13.	Certificate on CVC Guidelines:-

All CVC guidelines shall be adhered to while processing the case.

14.  Recommendation-

The estimate amounting to Rs. 188.78 Lacs for replacement of 33KV 400mm2 XLPE Cable from ESS Vidyut Bhawan to ESS School Lane and ESS School Lane to ESS Connaught Place, may be placed before the Council to accord administrative approval and expenditure sanction. Since the work is of urgent nature, approval is solicited to take further action in anticipation to confirmation of the Minutes of Council Meeting.

- Draft Resolution-

Resolved by the Council that Administrative approval & expenditure sanction is granted to the  estimate amounting to Rs. 1186.17 Lacs for replacement of 33KV, 400mm2 XLPE Cable from ESS Vidyut Bhawan to ESS School Lane and ESS School Lane to ESS Connaught Place. Further approval is accorded to take action and anticipation to confirmation of the Minutes of Council Meeting

COUNCIL’S DECISION

Resolved by the Council to accord administrative approval & expenditure sanction to the  estimate amounting to Rs.1186.17 Lacs for replacement of 33KV, 400mm2 XLPE Cable from ESS Vidyut Bhawan to ESS School Lane and ESS School Lane to ESS Connaught Place.

# It was also resolved that further action in the matter be taken in anticipation of confirmation of the minutes by the Council.