# ITEM NO. 25 (B-44)

Name of Subject:	Award of work for “Replacement of both 66KV circuits from G.T. Station to Sub-station Vidyut Bhawan NDMC.”

Name of Deptt:		Electricity Department.

Brief History of

the Case:	Both existing 66 KV circuits from G.T. Station to Sub-station Vidyut Bhawan are of 630 Sq. mm XLPE single core cable. Both these cables were initially laid by DVB and handed over to NDMC in January 2003 after unbundling of DVB.  These circuits are developing frequent faults.  Circuit No. 1 became faulty on 06.07.2005 and the same could not be revived as the same was not considered economically viable.  After lot of testing etc., this circuit was declared not fit for economical repairs and as such was abandoned.  The Circuit No. 2 is also in a very poor health and developed three major faults during summer 2007.  This second feeder is being kept in working order at reduced capacity of say about 50%.

An estimate amounting to Rs.28,05,84,000/- (G) and Rs.27,95,04,000/- (N) was accordingly prepared and sanctioned by Council vide Reso. No. 1 (B-13) dt. 24.01.2007.

An Expert Committee constituted under Shri Y.P. Singh, Chairman, ECGRF further recommended for immediate replacement of both these circuits on top priority.  For economical and technical reasons, both the existing 630 Sq. mm circuits have been proposed to be replaced with 1000 Sq. mm single core circuits  in line with suggestions of Director DTL (Operations).

#### Detailed proposal

#### on the Subject:	Sealed tenders giving wide publicity were invited for execution of above works.  There are only four firms in the country known to the department manufacturing 66 KV cables.  M/s Raychem RPG Ltd. & M/S Universal Cables Ltd. have submitted their offers as was observed while opening their Technical Bid on due date and time i.e. 16.11.2007.  These technical offers were examined and discussed in the TEC meeting dt. 28.12.07.  Both the firms were found at par meeting all the requirements of NIT and as such with the prior approval of Chairman NDMC dt. 02.01.2008, the Price Bids were opened on 03.01.2008 in the presence of representatives of both the firms.  The rates quoted by both the firms are as under: -

(i) M/s Raychem RPG Ltd. 		Rs. 16,03,23,606/-

(ii)M/s Universal Cables Ltd. 		Rs. 16,18,95,500/-

Evidentially, M/s Raychem RPG Ltd. were found to be the lowest firm.  The  justified  amount  prepared  by  the  department  comes  out  to Rs. 15,60,57,802/-.  So the rates quoted by the lowest firm are 2.73% above the justified rates.

Keeping in view the urgency of work, the department has recommended to award the work to the lowest firm.

Financial

Implications:			Rs. 16,03,23,606/-.

###### Implementation

Schedule:			Eight months from the date of Award of Work.

##### Comments of

Finance on the

subject:	Finance have examined the case and considering the urgency and background of the case have concurred in the proposal of the department to award the work for “Replacement of both 66KV circuits from G.T. Station to Sub-station Vidyut Bhawan NDMC.” to M/s Raychem RPG Ltd. being L-1 at their quoted rate amounting to Rs. 16,03,23,606/- (Rupees Sixteen Crore Three Lacs Twenty Three Thousand Six Hundred & Six Only) subject to the following: -

- Approval of competent authority.

- Available of funds.

- The tenderers have quoted Rs. 34.32 Lac for dismantling and making roll of existing 1c X 630 Sq. mm XLPE cable, department may certify whether retrieving would be economical.

## Comments of the

### Deptt. on the

### comments

of Finance:	Funds are available and the case is being noted to the Council for consideration and award of work.  This is further certified that only portions of the cables which can economically be dismantled shall only be allowed to be dismantled while getting the work  executed.

Legal

Implications:			NIL

Comments of			This has our concurrence.

Law Deptt.:

Comments of the

Deptt. on the

comments of 			NIL

Law deptt:.

Recommendations:	The case may be placed before the council for consideration and decision to award the work of “Replacement of both 66KV circuits from G.T. Station to Sub-station Vidyut Bhawan NDMC.” to M/S Raychem RPG Ltd. at their lowest quoted rates of Rs. 16,03,23,606/- (Rupees Sixteen Crores Three Lacs Twenty Three Thousand Six Hundred Six only) on the terms and conditions of NIT.

Draft Resolution:	Resolved by the Council that the work of “Replacement of both 66KV circuits from G.T. Station to Sub-station Vidyut Bhawan NDMC.” may be awarded to M/S Raychem RPG Ltd. at their lowest quoted rates of Rs. 16,03,23,606/- (Rupees Sixteen Crore Three Lac Twenty Three Thousand Six Hundred Six only) on the terms and conditions of NIT.  Since the works are of very urgent nature, the Council further resolved to award the works in anticipation to the confirmation of the minutes of the Council.

COUNCIL’S DECISION

Resolved by the Council that the work of replacement of both 66 KV circuits from G.T. Station to Sub-station Vidyut Bhawan, NDMC may be awarded to M/s Raychem RPG Ltd. at their lowest quoted rates of Rs.16,03,23,606/- on the terms and conditions of NIT.  Since the works are of very urgent in nature, the Council further decided to award the work, in anticipation of confirmation of the minutes, so as to complete the same by June 2008 end.