ITEM NO. 15 (B-39)

- Name of work- Establishing 33KV Electric Sub-Station at Raja Bazar.

- Name of the Department- ELECTRICITY DEPARTMENT

3.	Brief history of the proposals- The load of DIZ area, Gole Market, Baird Lane, Shivaji Stadium, Talkatora Stadium, Lady Harding Medical College Complex, State Emporia Buildings etc. is being fed from 33KV S/S Baird Lane and alternatively from S/S Hanuman Road. The S/S Baird Lane and S/S Hanuman Road are already operating at their maximum capacity. There is also a proposal for construction of new block in Lady Harding Medical College and hospital complex. Therefore, a new 33KV S/S has been proposed at Raja Bazar to meet the growing load demand of State Emporia Buildings and its adjoining area and new proposed buildings. This proposed 33KV S/S would relieve load on S/S Baird Lane.

The land for construction of 33KV Sub-station has already been allotted to NDMC by L&DO. The building plans have been finalized and drawings issued to Civil Engg. Department. The scheme is a part of Xth five-year plan, which has been technically cleared by CEA, vide No. DPD/UT/312(NDMC)/2005/43 dt. 29.3.06.

4.	Detailed proposal on the Project-

The following has been proposed in the estimate.

- 16/20MVA, 33/11KV Pr. Transformer – 2nos.

- 33KV, 1250 A, 1500 MVA, DBB Indoor Type GIS 7 Panel Board –      1 Bd.

- 11KV, 1250 A, 350 MVA, SBB Indoor Type SF-6/VCB 13 Panel Board- 2Bds.

- The S/S is proposed to be fed through 33KV, 3x400 Sq.mm XLPE Cable from 220KV S/S H.C. Mathur Lane (to be established by DTL) and 66KV S/S B.D. Marg.

The cost of the above equipments comes out to Rs. 1193.41 Lacs.

The cost of the construction of building, as intimated by Civil Engineering Deptt., is Rs. 133.59 Lacs.

Total estimated cost of the project comes out to Rs. 1327.00 Lacs including 3% contingencies. The scheme has now been out-sourced to M/s Power Grid Corp. of India Ltd. for turnkey execution of 33KV ESS.

5.	Financial Implications- The estimated cost for establishing 33KV S/S at Raja Bazar is Rs. 1327.00 lacs chargeable to the head of a/c E.4.1.

- Implementation schedule with timeliness for each stage including internal processing: - The scheme has been our-sourced to M/s PGCIL for turnkey execution and as per MOU completion time is 24-30 months.

7.	Comments of the Finance Department on the subject-

The finance deptt. has concurred in the preliminary estimate amounting to Rs. 1327.00 lacs subject to-

  - Department has not recorded the basis on which lump sum provision of Rs. 123.29 lacs in r/o items 2 (i), 2(ii) and 2(iii) has been kept in the estimate despite our observations dated 2.11.07.  Since it is not a small amount; provisions for these items needs to be kept after preparing analysis of rates after ascertaining market rates as amount involved in lump sum provision is not a small sum.

  - Neither CEE; nor SE(P) has put his signature at pages 61,64,65 and 67/C of the estimate.  This may be done now.

    - Approval of the competent authority.

    - Availability of funds.

iii) Certification by the department that the work would be got                 executed after adhering the codal provisions.

- Comments of the Department on comments of Finance Deptt:

  - As mentioned in CPWD Works Manual-2003, Clause 4.1, the Preliminary estimate is prepared for ready and rough calculation, so as to give an approximate idea of the cost involved in the proposal.   However the work has been out-sourced to M/s PGCIL for turnkey execution of the work.

  - CEE & SE (P) has now signed the estimate.

  - 1. Approval of the competent authority being sought.

2. Rs. 3.60 crores has been kept for this work in the RE 2007-08   and suitable provision will be kept in the subsequent years.

3. The work has been out-sourced to the PGCIL and execution will be done as per codal provision.

- Legal implications of the Project: - No legal implication is involved.

10.	Details of Previous Council Resolution- Nil

11.	 Comments of the Law Deptt. on the Project: No legal point involved.

12. Comments of the deptt. on the Law Deptt:  NIL

13. Recommendation- The case may be noted to the Council for sanction of the estimate amounting to Rs. 1327.00 lacs and also be accord administrative approval and expenditure sanction for the estimated amount for establishing 33KV ESS at Raja Bazar.  The work has been out-sourced to M/s PGCIL for turnkey execution of the work.

14. Draft Resolution- Resolved by the Council that the estimate amounting to Rs. 1327.00 lacs is sanctioned and A/A & E/S accorded for the estimate amount for establishing 33KV Electric Sub-Station at Raja Bazar. The work has been out-sourced to M/s PGCIL for turnkey execution of the work.

COUNCIL’S DECISION