ANNEXURE – V

ITEM NO. 25 (B-14)/15/22.07.2009

- Name of work- Establishing 33KV Electric Sub-Station at Aliganj Jorbagh

- Name of the Department- ELECTRICITY DEPARTMENT

- Brief history of the proposals-

CPWD is re-developing the area of Ali Ganj Jorbagh. The load demand of the proposed housing complex scheme is to the tune of 6.3MVA (app.), as worked out as per new yard stick which may increase with time. As per NDMC policy resolved vide Reso. No. 6(iv) dated 20.4.01, If the consumer has load demand of more than 4 MVA, 33KV ESS is required to be established.

Load of the area is increasing day–by-day; as it is surrounded by the resident of diplomats alongwith Schools, Community Centre, Barat Ghars and residence complex of NDMC. Presently,  load requirement of the area is being fulfilled by 66KV ESS Vidyut Bhawan and 33KV ESS Rajiv Gandhi Bhawan through 11KV ESS at Ali Ganj Jorbagh-I & II, Lodhi Road I & II and Aurbindo Marg.

The existing 11KV System would not be able to meet the load demand of the proposed GPRA project of CPWD since 11KV ESS are already being operated at their maximum capacity. Keeping in view the system constraints a 33KV ESS is essentially required to be established in the area. The proposed 33KV ESS will relieve load on existing 33KV and 66KV S/S Vidyut Bhawan.

Accordingly CPWD was requested to make provision of land for establishing 33/11KV ESS in their proposed complex. CPWD has earmarked a plot measuring 1500 Sq.Mt. in their lay out  plan which is submitted to the L&DO and matter for allotment of land to NDMC for proposed 33KV ESS is being persued with L&DO.

The scheme is a part of XIth five-year plan, which has been technically approved by CEA vide No. DPD/UT/312(NDMC) 2007/436 dated 26.06.07.The scheme has outsourced to PGCIL for turnkey execution.

4.	Detailed proposal on the Project-

To meet the load demand  following have been  proposed in the estimate.

- 16/20MVA, 33/11KV Pr. Transformers 			- 2 Nos.

- 33KV, 1250 A, 1500 MVA, SBB  Indoor Type

GIS 7 Panel Board 					- 1 No.

- 11KV, 1250 A, 350 MVA, SBB Indoor Type

SF-6/VCB 13 Panel Board 				- 2 Nos.

- 1000KVA, 10.5/0.415 KV, oil  type,

Distribution Transformer 				 -2 Nos.

- Two Tier LT Panel Board with ACB			 -1 No.

- The S/S is proposed to be fed through 33KV, 3x400 Sq.mm XLPE Cable from 220KV Substation Trauma Centre, AIIMS and 66KV Substation Vidyut Bhawan.

Accordingly a preliminary estimate amounting to Rs. 1450.64 Lacs including 3% contingencies has been prepared to cover the cost of the above work including the cost of the building and allied works.

5.	Financial Implications- The estimated cost for establishing 33KV S/S at Aliganj Jorbagh is Rs. 1450.64 lacs chargeable to the head of a/c E.4.1.

- Implementation schedule with timeliness for each stage including internal processing: - The scheme has been outsourced to M/s Power Grid Corporation of India Limited for turnkey execution and as per MOU completion time is 24-30 months.

- Comments of the Finance Department on the subject-

The finance Deptt. has concurred in the preliminary estimate amounting to Rs.1450.64 lacs subject to-

  - Approval of the competent authority.

  - Availability of funds.

  - The department may bring on record the action being taken on the advice of Advisor (Power) given earlier about streamlining the procedure for framing the estimate for spare and for erection in NDMC in consultation with M/s DTL & CEA.

  - The work would be got executed after adhering codal provisions.

  - As informed by the department at page 7/N that the preparation of estimate is not the part of the turnkey agreement with PGCIL, therefore the detailed estimate for the work would be prepared by the department on the basis of proper analysis of the rates.

  - Cost; if any; for establishing of 33KV ESS recoverable from CPWD in the light of resolution no.3 (iv) dated 20.04.01 referred to by the department at portion marked ‘A’ on page 1/N may be recovered.

- Comments of the Department on comments of Finance Deptt:

Observation of Finance Deptt. are clarified as under:-

- Approval of the competent authority i.e. Council is being sought.

- Rs.200 Lacs has been kept in the BE 2009-10. The budget shall be suitably revised in RE-2009-10 and subsequent years as per future requirement.

- The advice of Advisor (Power) is being examined.

- The codal provisions would be adhered to.

- The detailed estimate shall be prepared by the PGCIL / executing division on the basis of proper analysis of rates.

- Vide Council res. No. 3(IV) Dt. 20.04.2001 at Para-3 and Sub-para-4 i.e. The entire cost of establishing 66/33 KV Sub-station shall be borne by NDMC.  However, cost of 11KV connection on LT connection as the case may be, shall be borne by the consumer as per 11KV policy.

Finance have seen above comments of the Deptt. & have offered no further comments.

- Legal implications of the Project: -  Nil

10.	Details of Previous Council Resolution- Nil

11.	 Comments of the Law Deptt. on the Project: NIL

12.   Comments of the Deptt. on the Law Deptt   NIL

13.  Recommendation:- The preliminary estimate amounting to Rs. 1450.64 Lacs for establishing 33KV ESS at Aliganj Jorbagh, may be placed before the Council to accord administrative approval and expenditure sanction. Since the work is of urgent nature and outsourced to M/S PGCIL, approval may also be solicited to take further action in anticipation to confirmation of the Minutes of Council Meeting..

14.   Draft Resolution:- Resolved by the Council that Administrative approval & expenditure sanction is granted to the preliminary  estimate amounting to Rs. 1450.64 Lacs for establishing 33KV Electric Sub-Station at Aliganj Jorbagh. Further approval is accorded to take action and anticipation to confirmation of the Minutes of Council Meeting

COUNCIL’S DECISION

Resolved by the Council to accord administrative approval & expenditure sanction to the preliminary  estimate amounting to Rs.1450.64 Lacs for establishing 33KV Electric Sub-Station at Aliganj, Jorbagh.

It was also resolved that further action in the matter be taken in anticipation of confirmation of the minutes by the Council.