ITEM NO. 6 (B-1)

l. 	Name of the Project:- 	Providing 66KV Feeders (4X630Sq.mm single core for each S/S) from S/S Park Street to S/S School Lane & S/S Vidyut Bhawan

2. 	Name of the Department Concerned:- Electricity Department

3. Brief history of the project:-  At present installed transformer capacity of S/S School Lane & S/S Vidyut Bhawan is 140MVA at each S/Stn. The present feed to each of these sub-station is from G.T. Station of DTL. The feeder capacity at each of these sub-stations. Through double circuit 630 sqmm. S/C Aluminium conductor XLPE cable is about 90 MVA. Thus NDMC is not able to utilize the full transformer capacity at any of these two sub-stations. Moreover in case of any fault or breakdown at G.T. Station or in the cable from G.T. Station, the supply cannot be restored from any alternate source. The matter was taken up in the Steering Committee Meeting as well as in DERC and after a lot of persuasion DTL has agreed to provide two bays as alternate source of supply from S/S Park Street. With the above proposed arrangement, NDMC will not only be able to utilize full transformer capacity at each of these sub-stations but will also be able to get alternate source of supply at each of these two sub-stations.

4. Detailed proposal on the Project: - Originally, 66KV Feeder of size 3x630sqmm. Single core XLPE insulated Aluminum conductor cable was proposed to be laid from S/S Park Street to S/S School Lane & S/S Vidyut Bhawan.  The estimate amounting to Rs. 13.17 crore for the same was approved by the Council vide Reso. No. 9(B-16) dt. 13.2.2006. The scheme was reviewed by the CEA and vide its letter No.DPD/UT/312(NDMC)/2005/43 dated 29.3.06 had suggested that 4 lengths of 66KV XLPE single core cable from Park Street to School Lane and Park Street to Vidyut Bhawan might be laid in place of 3 lengths for meeting any contingencies in future.  Subsequently, the meeting taken by Member (GO&D), CEA on 26.5.06, (minutes circulated vide letter No. DPD/UT/315(Delhi)/2006/97 dated 5.6.06) it was decided that the estimate may be revised for laying 4 lengths of 66KV cable.

Further in this regard E-in-C, NDMC has also taken the meeting on 16.10.06 with Director (UT) CEA and it was decided that the 4th cable may be laid and the works may be started.  Meanwhile, the estimate may be revised for taking approval of the competent authority for administrative approval and expenditure sanction.  The work has been taken in hand.  CEA has been approached to provide consultancy for the work.  DTL is being vigorously followed up to make available two new bays for NDMC at 220KV S/S Park Street.

Accordingly the estimate has been revised amounting to Rs.17.39 Crores including 3% contingencies to cover the cost of the above work.

The expenditure shall be chargeable to the original works under the head of A/c E-4-1 for which a budget provision of Rs.13 Crores has been kept during the year 2007-08

5. Financial implications of the proposed project:-

The revised estimated cost for laying of 66KV feeders from S/S Park Street to S/S School Lane & S/S Vidyut Bhawan is Rs.17.39 Crores. The expenditure shall be chargeable to the original works under the head of A/c E-4-1 for which a budget provision of Rs.13 Crores has been kept during the year 2007-08

6.	Implementation schedule with timeliness for each stage including internal processing:-

i)	Approval of scheme by Council 	       March-2007

- Issue of estimate to construction.		Division for execution	                        Work already taken up 				by Project  Division

iii)  Preparation of draft NIT	        April-2007

iv)  Call of tenders	        May- 2007

v)   Award of work including                 	        October-07

opening of tenders, negotiation

with the  tenderer etc.

vi) Completion of work	         August,08

The above implementation schedule is subject to the condition that the two bays at S/S Park Street are made available by DTL by May,07

7.	Comments of the Finance Deptt. on the subject:-

The Finance Deptt. has concurred to the  proposed estimate subject to

i)	Approval of the competent authority.

ii)	Availability of funds.

iii)	The department would furnish the schedule of the completion of the work while obtaining the approval of the competent authority.  A copy of the same be also furnished to the Finance Department.

iv) Work will be executed by adhering all the Codal provisions.

v) Confirmation of facts and figures.

vi) Signature of competent authority on the estimate as a token of acceptance.

8.	Comment of the Deptt. on comments of Finance Deptt.:-

i)	The necessary approval being sought from competent authority.      ii)	Suitable provision kept in the R.E. 2006-07 & B.E.2007-08 and will

be kept in subsequent Budget Estimates

iii) Schedule of the completion of the work is mentioned above.

iv) The work would be executed by the executing division as per Codal

provisions.

v) 	Facts and figures are correct.

vi)The estimate has been signed by SEE(P).

9.	Legal implication of the Project: -

No legal implication is involved.

10.	Details of previous Council resolution:-

ItemNo.9(B-16)   dated 13.2.06

11.	Comments of the Law Deptt. on the project:-

N.A.

12.	Comments of the Deptt. on the comments of Law Deptt.:-

Nil

13.	Recommendation:-

The case may be noted to the Council for sanction of revised estimate amounting to Rs. 17.39 Crores and also be accord administrative approval and expenditure sanction for the estimated amount.

14.	Draft Resolution:-

Resolved by the Council that revised estimate amounting to Rs. 17.39 Crores is sanctioned and A/A & E/S accorded for the estimated amount for “Providing of 66KV feeders (4X630Sq.mm single core for each S/S) from S/S Park Street to S/S School Lane & S/S Vidyut Bhawan”.

COUNCIL’S DECISION

Resolved by the Council that revised estimate amounting to Rs. 17.39 Crores is sanctioned and administrative approval and expenditure sanction is accorded for the estimated amount for “Providing of 66KV feeders (4X630Sq.mm single core for each S/S) from S/S Park Street to S/S School Lane & S/S Vidyut Bhawan”.