ITEM NO. 03 (B-16)

(1) Name of the Project :	Replacement of existing HT PILCA cable  size 300sqmm/3C with HT XLPE size 400 sqmm/3C from Electric Substation Kidwai Nagar(W) to Electric Substation Nehru Park via Electric Substation Booster Pump Sarojini Nagar.

(2) Name of the Department  :  Electricity (11 KV Planning)

(3) Brief History of the Project :

HT PILCA cable size 300 sq. mm/3C  was laid from Electric Substation Kidwai Nagar (West) to Electric Substation Nehru Park via Electric Substation Booster Pump Sarojini Nagar in 1986. E.E.(M/S) has informed that this cable has served for 20 years only against its prescribed life of 35 years, but needs to be replaced immediately as a number of joints have been made in this cable due to digging work carried out by various Agencies like; MTNL, IGL, NDMC (Civil Engg. Deptt. & Water Supply Deptt.).  This cable has become so weak that it cannot take continuous load in peak hours during summer season.  In case of failure of this HT cable due to one reason or the other, it becomes difficult to restore the supply in the residential quarters in Sarojini Nagar area as well as supply to the Booster Pump, Sarojini Nagar is also effected.  In case this cable is loaded to 75% of its capacity in summer season  the feeder becomes faulty very frequently.  E.E.(M/S) has therefore proposed to replace this cable with HT XLPE cable size 400 sq.mm/3 C.

Accordingly an estimate amounting to Rs. 55,35,000/- has been framed for replacement of existing  HT PILCA cable  of size 300 sq. mm/3C with HT XLPE cable size 400 sq.mm/3C from Electric Substation Kidwai Nagar (West) to Electric Substation Nehru Park via Electric Substation Booster Pump Sarojini  Nagar.

(4)  Detailed proposal on the Project :

| (a) | The existing system : | Existing HT PILCA cable of size 300 sq. mm/3C with HT XLPE cable size 400 sq.mm/3C from Electric Substation Kidwai Nagar (West) to Electric Substation Nehru Park via Electric Substation Booster Pump Sarojini Nagar |
| --- | --- | --- |
| (b) | Deficiencies of the existing system : | This cable has served for 20 years only against its prescribed life of 35 years, but needs to be replaced immediately as a number of joints have been made in this cable due to digging work carried out by various Agencies like; MTNL, IGL, NDMC (Civil Engg. Deptt. & Water Supply Deptt.). This cable has become so weak that it cannot take continuous load in peak hours during summer season |
| (c) | Extent of utilization of existing system : | Existing cable will be dismantled to the extent viable. |
| (d) | Necessity of augmentation of the system : | To restore the supply in the residential quarters in Sarojini Nagar area as well as supply to the Booster Pump, Sarojini Nagar |
| (e) | Technical viability of the proposed scheme : | The scheme has been technically cleared by the then C.E.(E)II. |

The following has been proposed in the estimate :

Replacement of existing  HT PILCA cable  of size 300 sq. mm/3C with HT XLPE cable size 400 sq.mm/3C.

(5)	Financial implications of the proposed project : An estimate amounting to Rs. 55,35,000/- has been framed for replacement of existing  HT PILCA cable  of size 300 sq. mm/3C with HT XLPE cable size 400 sq.mm/3C from Electric Substation Kidwai Nagar (West) to Electric Substation Nehru Park via Electric Substation Booster Pump Sarojini  Nagar.  The Expenditure shall be charged  to the Head : E-3  “Replacement of old 11 KV cables, LT cables, service lines and meter boards” for which a provision of Rs. 200 lacs has been approved vide Budget Book 2007-08 Page No. 134 item No. 2 and shall be revised suitably during R.E. 2007-08.

(6)	Implementation schedule with timeliness for each stage including internal processing :

The work is likely to be completed by March, 2008, however the completion of work depends on a number of factors like; availability of cable in Store, valid annual cable laying contract etc. etc.

(7)	Comments of the Finance Deptt. on the subject :

The Finance Deptt. has concurred in to the proposed estimate vide No. 1283/Finance dated 18-6-07 subject to :

i)	     Availability of funds.

- Approval of the Competent Authority.

- Correctness of information and data submitted by the Deptt.

- Codal provision shall be adhered during execution of the work.

- The Project Report be got signed by SEE(P).

- Department must ensure that the electric cables are not damaged in the process of road digging and the suggestions made at S.No.1&2 of page 12/N be followed which has the approval of Chairperson dated 7-12-06.

(8)	Comments of the Deptt. on comments of Finance Deptt.

- Funds are available. The Expenditure shall be charged  to the Head : E-3  “Replacement of old 11 KV cables, LT cables, service lines and meter boards” for which a provision of Rs. 200 lacs has been approved vide Budget Book 2007-08 Page No. 134 item No. 2 and shall be revised suitably during R.E. 2007-08.

- Necessary approval is being sought from the competent authority.

- Information and data submitted by the deptt. are correct.

- The work would be executed by the executing division as per the Codal provision.

- Project report has been signed by SEE(P).

- Due precautions shall be taken.

(9)	Legal implication of the Project : No legal implication is involved.

(10)	Details of previous Council Resolution :	N.A.

(11)	Comments of  L.A.  on the project :

Law Deptt. has opined that “it is observed that no law point is involved in this matter, therefore, this has our concurrence.”

(12)	Recommendation : The case may be noted to the Council for sanction of estimate amounting to Rs. 55,35,000/-  (Rupees Fifty five lakh thirty five thousand only)  for replacement of existing  HT PILCA cable  of size 300 sq. mm/3C with HT XLPE cable size 400 sq.mm/3C from Electric Substation Kidwai Nagar (West) to Electric Substation Nehru Park via Electric Substation Booster Pump Sarojini  Nagar and also to accord administrative approval and expenditure sanction to the estimate.

(13)	Draft Resolution : Resolved by the Council that estimate amounting to Rs. 55,35,000/-  (Rupees Fifty five lakh thirty five thousand only) is sanctioned and A/A & E/S accorded  for replacement of existing  HT PILCA cable  of size 300 sq. mm/3C with HT XLPE cable size 400 sq.mm/3C from Electric Substation Kidwai Nagar (West) to Electric Substation Nehru Park via Electric Substation Booster Pump Sarojini  Nagar

COUNCIL’S DECISION